ME 576 Lab. Assignment No. 13

DC/AC Motors


Part A:
 AC Motor (Induction Motor with PWM)

This week’s laboratory involves experimenting with the three-phase AC motor control kit.  The purpose of this exercise is to give students hands-on experience of a new method of speed control used for industrial motors.  Students will learn electrical and mechanical characteristics of AC motors driven by pulse-width-modulated (PWM) waveforms and observe how feedback control can help to maintain a constant speed in the presence of disturbances such as the change of load and inertia.  First, go through the handout that explains the basic theories regarding the AC motor control kit.  Then, follow the procedures given below.  You must be under the supervision of the TA whenever you try to make a change in the wiring of the equipment.  Before starting each part of the experiment, check to see if the equipment is switched on and adjusted to match the standard control setting as in Table 1.  Your lab. report should include detailed observations made during the lab. and discussions.
Part 1. Voltage, Current, Speed and Frequency Characteristics of AC Motor

1) Observation of pulse-width-modulated motor voltage waveforms

You will have a chance to observe the switched voltage waveform in the AC motor.  First, Switch off the power.  Make sure there is no connection to any 0V socket of the PE 485 kit.  Connect channel 1 of the oscilloscope between two phases of the motor, say V and W using the 10:1 probe.  Set the oscilloscope according to the following table:

	Time scale
	Voltage scale
	Coupling
	Trigger source

	2 ms/div
	20.0 V/div
	DC
	Channel 1


Switch on the power, switch to ‘run’ and raise the frequency to about 40Hz. Adjust the oscilloscope and the frequency until you get a steady trace.  Observe the waveform, and then make a sketch or print-out.  Try varying the frequency and observe how the waveform changes. 

2) Observation of motor current waveforms

You can use special sockets in PE485 kit to provide a copy of the current waveform as a voltage referred to the 0V line.  Switch off the power.  Remove the wiring made to the two phase of the motor in the previous assignment.  Connect the external sync input of the oscilloscope to ‘sync output’ of PE485A.  Connect the two input channels to the PE485B sockets I1 and I2.  Use 0V lines of PE485 to supply ground to the oscilloscope.  Set the oscilloscope according to the following table:

	Time scale
	Voltage scale
	Coupling
	Trigger source

	5 ms/div
	100 mV/div
	AC
	External


Switch on the power, switch to ‘run’ and raise the frequency to about 40Hz.  Observe the waveforms and relative phase.  Try connecting I1 - I3, I2 - I3 and see how they are spaced in phase.  They will be similar waveforms, nominally sinusoidal and 120o apart in phase.  Make a sketch or print-out.  Explain how the switched voltage waveforms observed in the previous section can generate a smooth sinusoidal current waveforms.

3) Electro-mechanical behavior of AC motor

In this section, you will discover how the voltage, current and speed of the motor vary as the speed setting is changed and see the effect of a mechanical load on the motor.  Switch off the power.  Connect the DMMs according to Fig. 1 and set the ranges.  Switch on the power.  Switch the stop/run switch to ‘run’. By adjustment of the set speed control, raise the output frequency to 30Hz.  Adjust the voltage VCO control to give a 30V reading on meter 2. Then set the frequency back to zero.  

Use the table in Fig. 2 to enter your results in.  In the left-hand column of the results table a number of frequency values are listed.  Set the frequency to each of these values in turn, using the set speed control, and record under the heading ‘No load’:

· The motor voltage – meter 2

· The motor current – meter 4

· The tachogenerator current – meter 1.

Each tachogenerator reading should be converted into speed.  The scaling factor is 5000 rev/min per mA.  Note that, in order to go above 100Hz, you will have to adjust the gain control slightly.  Plot your results on a graph.  Figure 3 shows an example of the graph.  Your results should show electrical behavior that can be classified into three regions as in the handout.

After you have completed the ‘No Load’ readings, rotate the magnet assembly to position 10 on its scale.  Take a second set of readings to complete the ‘Loaded’ columns of the results table, reducing the frequency in steps.  You may notice that the loaded speed reading for 120Hz is less than that for 100Hz.  Look at the torque-speed graph in the handout and discuss the results.

Part 2. Closed-Loop Speed Control

This part of the lab. is aimed at investigating the advantage of closed-loop control in dealing with external disturbances.  The following figure shows the schematic of closed-loop speed control.

[image: image1.png]This amplifier compares Motor controlled by
the set and measured difference signal

speeds
frequency
VCO

Set
Speed

motor tachogenerato!

inverter
system

measured speed signal




Switch off the power. Connect the DMMs according to Fig. 4 and set the ranges.  Note that the other end of meter 4 should be connected to the power supply.  Swing the magnet away from the brake disc.


Set the deceleration control to mid-range and switch the dynamic brake switch ‘on’.  Use the results sheet in Fig. 5.


Switch on. Use the stop/run switch and the set speed control to run the motor with an indicated frequency of 50Hz.


On the ‘No-Load’ row of the results sheet, record the values of the current shown by meter 1 and meter 4.  Take particular care to read meter 1 precisely. Convert the speed in rev/min.


Apply breaking by rotating the magnet assembly to mark 6 on its scale.  Record a new set of readings as before, in the ‘Open Loop’ row of the results table. Record the frequency.  This completes the open loop measurements.


Close the loop by switching the tacho switch ‘on’.  To complete the results table the following procedure is given.

1. Swing the magnet assembly away from the break disc.  Bring the output frequency back to 50Hz.

2. Check that the unloaded conditions are as you recorded them before. Then apply braking to mark 6 and record a new set of readings.


The first time, setting the 50Hz will probably require the set speed control to be turned fully clockwise, after which a slight adjustment of the gain control may be necessary to get the minimum gain at which 50Hz can be set.  Record the results in the ‘minimum gain’ low.


The second time, set the gain control mid-way between that minimum gain position and ‘max’.  Then adjust the set speed control for 50Hz.


Finally set the gain control to ‘max’.  Then adjust the set speed control for 50Hz. Your results should show that when the tachogenerator feedback is operating, the fall in speed due to applied load is reduced.  Explain why setting the gain to maximum may not be the best way to control.

Table 1. Standard control setting

	Control to set
	Standard control setting

	Acceleration
	Min (fully counterclockwise)

	Deceleration
	Min

	Stop/run
	Run while setting; leave at stop

	Delay oscillator
	Fully clockwise

	Set speed
	mid-scale

	Gain
	Min

	Frequency VCO
	50Hz output

	Voltage VCO
	43V between motor phases

	Tacho
	Off

	Boost switch
	Off


[image: image2.png]




Fig. 1 Connections for section 1-3.

[image: image3.png]No Load Loaded
Frequency)| Motor Tacho Speed Motor | Tacho | Speed

Hz mA rev/min A mA | revimin
VIA

5
10
20

30

40
50
60
80
100

120




Fig. 2 Results sheet for section 1-3.

[image: image4.png]frequency, Hz

40 60 80 100 120

20




Fig. 3 Graph sheet for results

[image: image5.png]meter 4

PE485A

PE48SC

= Feedback





Fig. 4 Connections for Part 2.

[image: image6.png]Tacho | Speed | Speed [Frequency| Current
Condition mA | rev/min | Change Hz A

Loaded

T ——
) B I

CT I N





Fig. 5 Results sheet for Part 2.

 Range:


 50V AC





 Range:


 1mA DC





 Range:


 2A AC





 Range:


 50V AC





 Range:


 2A AC





 Range:


 1mA DC








