## Slide 1: DESIGN OF MEMBERS FOR COMBINED FORCES
CE 470: Steel Design
By:
Amit H. Varma

## Slide 2: Design of Members for Combined Forces
Chapter H of the AISC Specification
This chapter addresses members subject to axial force and flexure about one or both axes.
H1 - Doubly and singly symmetric members
  H1.1 Subject to flexure and compression
  The interaction of flexure and compression in doubly symmetric members and singly symmetric members for which 0.1  Iyc / Iy  0.9, that are constrained to bend about a geometric axis (x and/or y) shall be limited by the Equations shown below.
  Iyc is the moment of inertia about the y-axis referred to the compression flange.

## Slide 3: Design of Members for Combined Forces
where,
x = subscript relating symbol to strong axis bending
y = subscript relating symbol to weak axis bending

## Slide 4: Design of Members for Combined Forces
Pr = required axial compressive strength using LRFD load combinations
Mr = required flexural strength using LRFD load combinations
Pc = c Pn = design axial compressive strength according to Chapter E
Mc = b Mn = design flexural strength according to Chapter F.
c = 0.90 and b = 0.90

## Slide 5: Design of Members for Combined Forces
H1.2 Doubly and singly symmetric members in flexure and tension
  Use the same equations indicated earlier
  But, Pr = required tensile strength
  Pc = t Pn = design tensile strength according to Chapter D, Section D2.
  t = 0.9
  For doubly symmetric members, Cb in Chapter F may be multiplied by for axial tension that acts concurrently with flexure
    Where, ; α=1(LRFD)

## Slide 6: Design of Members for Combined Forces
H1.3 Doubly symmetric rolled compact members in single axis flexure and compression
  For doubly symmetric rolled compact members with in flexure and compression with moments primarily about major axis, it is permissible to consider two independent limit states separately, namely, (i) in-plane instability, and (ii) out-of-plane or lateral-torsional buckling.
  This is instead of the combined approach of Section H1.1
  For members with, Section H1.1 shall be followed.

## Slide 7: Design of Members for Combined Forces
  For the limit state of in-plane instability, Equations H1-1 shall be used with Pc, Mrx, and Mcx determined in the plane of bending.
  For the limit state of out-of-plane/lateral torsional buckling:
  where:
  = available compressive strength out of plane of bending
  = lateral torsional buckling modification factor (Section F1)
  available lateral-torsional strength for strong axis flexure (Chapter F, using =1)

## Slide 8: Design of Members for Combined Forces.
The provisions of Section H1 apply to rolled wide-flange shapes, channels, tee-shapes, round, square, and rectangular tubes, and many other possible combinations of doubly or singly symmetric sections built-up from plates.
cPY
bMp
Section P-M interaction
For zero-length beam-column
cPY

## Slide 9: Design of Members for Combined Forces.
P-M interaction curve according to Section H1.1
cPn
bMn
P-M interaction
for full length
cPn
Column axial load capacity
accounting for x and y axis buckling
Beam moment capacity
accounting for in-plane behavior
and lateral-torsional buckling
P-M interaction
for zero length
bMp
cPY

## Slide 10: Design of Members for Combined Forces.
P-M interaction according to Section H1.3
cPnx
bMn
P-M interaction
In-plane, full length
cPnx
Column axial load capacity
accounting for x axis buckling
In-plane Beam moment capacity
accounting for flange local buckling
P-M interaction
for zero length
bMp
cPY
cPny
Out-of-plane Beam moment capacity
accounting for lateral-torsional buckling
P-M interaction
Out-plane, full length
Column axial load capacity
accounting for y axis buckling

## Slide 11: Design of Members for Combined Forces.
Steel Beam-Column Selection Tables
Table 6-1 W shapes in Combined Axial and Bending
The values of p and bx for each rolled W section is provided in Table 6-1 for different unsupported lengths KLy or Lb.
The Table also includes the values of by, ty, and tr for all the rolled sections. These values are independent of length

## Slide 12: Design of Members for Combined Forces.
Table 6-1 is normally used with iteration to determine an appropriate shape.
After selecting a trial shape, the sum of the load ratios reveals if that trial shape is close, conservative, or unconservative with respect to 1.0.
When the trial shape is unconservative, and axial load effects dominate, the second trial shape should be one with a larger value of p.
Similarly, when the X-X or Y-Y axis flexural effects dominate, the second trial shape should one with a larger value of bx or by, respectively.
This process should be repeated until an acceptable shape is determined.

## Slide 13: Estimating Required Forces - Analysis
The beam-column interaction equation include both the required axial forces and moments, and the available capacities.
The available capacities are based on column and beam strengths, and the P-M interaction equations try to account for their interactions.
However, the required Pr and Mr forces are determined from analysis of the structure. This poses a problem, because the analysis SHOULD account for second-order effects.
1st order analysis DOES NOT account for second-order effects.
What is 1st order analysis and what are second-order effects?

## Slide 14: First-Order Analysis
The most important assumption in 1st order analysis is that FORCE EQUILIBRIUM is established in the UNDEFORMED state.
All the analysis techniques taught in CE270, CE371, and CE474 are first-order.
These analysis techniques assume that the deformation of the member has NO INFLUENCE on the internal forces (P, V, M etc.) calculated by the analysis.
This is a significant assumption that DOES NOT work when the applied axial forces are HIGH.

## Slide 15: First-Order Analysis
P
P
M1
M2
Results from a 1st order analysis
V1
-V1
M1
M2
Moment diagram
M(x)
x
Free Body
diagram
In undeformed state
Has no influence of deformations or axial forces
M(x) = M1+V1 x

## Slide 16: Second Order Effects
x
Free Body
diagram
In deformed state
v(x) is the vertical deformation
Includes effects of deformations & axial forces
P
P
M1
M2
V1
-V1
M(x)
P
M1
V1
M(x) = M1+V1 x + P v(x)
M1
M2
Moment diagram

## Slide 17: Second Order Effects

## Slide 18: Second Order Effects
Clearly, there is a moment amplification due to second-order effects. This amplification should be accounted for in the results of the analysis.
The design moments for a braced frame (or frame restrained for sway) can be obtained from a first order analysis.
  But, the first order moments will have to amplified to account for second-order effects.
  According to the AISC specification, this amplification can be achieved with the factor B1

## Slide 19: Second Order Effects
  Pe1 = 2EI/(K1L)2
  I =moment of inertia in the plane of bending
  K1=1.0 for braced case

## Slide 20: Second Order Effects
Sign Convention for M1/M2

## Slide 21: Further Moment Amplification
This second-order effect accounts for the deflection of the beam in between the two supported ends (that do not translate).
  That is, the second-order effects due to the deflection from the chord of the beam.
When the frame is free to sway, then there are additional second-order effects due to the deflection of the chord.
  The second-order effects associated with the sway of the member () chord.

## Slide 22: Further Moment Amplification
Mo
P
Mo
P
D
Mo
Mo
+
P D
=
Mmax
As you can see, there is a moment amplification due to the sway of the beam chord by .
This is also referred as the story P- effect that produces second-order moments in sway frames due to inter-story drift.
All the beam-columns in the story will have P- effect

## Slide 23: Further Moment Amplification
The design moments for a sway frame (or unrestrained frame) can be obtained from a first order analysis.
  But, the first order moments will have to amplified to account for second-order P- effects.
  According to the AISC specification, this amplification can be achieved with the factor B2

## Slide 24: Further Moment Amplification

## Slide 25: The final understanding
The required forces (Pr, Vr, and Mr) can be obtained from a first-order analysis of the frame structure. But, they have to be amplified to account for second-order effects.
  For the braced frame, only the P- effects of deflection from the chord will be present.
  For the sway frame, both the P- and the P- effects of deflection from and of the chord will be present.
These second-order effects can be accounted for by the following approach.
  Step 1 - Develop a model of the building structure, where the sway or interstory drift is restrained at each story. Achieve this by providing a horizontal reaction at each story
  Step 2 - Apply all the factored loads (D, L, W, etc.) acting on the building structure to this restrained model.

## Slide 26: The final understanding
Step 3 - Analyze the restrained structure. The resulting forces are referred as Pnt, Vnt, Mnt, where ‘nt’ stands for no translation (restrained). The horizontal reactions at each story have to be stored
Step 4 - Go back to the original model, and remove the restraints at each story. Apply the horizontal reactions at each story with a negative sign as the new loading. DO NOT apply any of the factored loads.
Step 5 - Analyze the unrestrained structure. The resulting forces are referred as Plt, Vlt, and Mlt, where ‘lt’ stands for lateral translation (free).
Step 6 - Calculate the required forces for design using
Pr = Pnt + B2 Plt
Vr = Vnt + B2 Vlt
Mr = B1 Mnt + B2 Mlt

## Slide 27: Example